## Slide 1: ASSE-III Final (2020/2021)
Spring- 2021
Presenters:
Yousef Yaish | 201701045
Majed Daher | 201300947
Othman Al- awad | 201600457
1
Supervisor’s Name: Dr. Saidur Chowdhury
Coordinator’s Name: Dr. Andi Asiz

## Slide 2
DESIGN OF WASTEWATER TREATMENT PLANT IN AL-JUBAIL INDUSTRIAL CITY

## Slide 3: OUTLINE
Introduction and Objectives
Project Constraints and Complexities
Codes and Specifications
Design Methodology
Environmental Impact Assessment (EIA)
Design Calculations
Structural and Hydraulic Design
Software Model
Cost Estimation Analysis
Summary and Conclusion
References
(Martina, Nolte, 2012)

## Slide 4: INTRODUCTION
Global water has been consumed more rapidly over the course of the last few years, and more of the population need to consume it for various reasons.
Industrial wastewater treatment consists of various processes to remove various contaminants from wastewater.
Wastewater treatment plant is important as any other necessary facility to build a healthy society or a city.

## Slide 5: OBJECTIVES
To choose a location in Al-Jubail industrial area to treat the wastewater from nearby factories.
To design the three main units required for the WWTP which are aeration, sedimentation, and filtration tanks.
To estimate the cost of the plant.

## Slide 6: BACKGROUND

## Slide 7: BACKGROUND

## Slide 8: BACKGROUND Table 3.1: Classification of Untreated Industrial Wastewater. (Ilgi, Karapinar, 2005)
Parameter | Range | Average
pH | 9.12 – 9.6 | 9.3
Temperature (◦C) | 35 – 42 | 39
Iron (mg/L) | 0.83 – 2.12 | 1.2
𝐂𝐥−(mg/L) | 17750 – 34000 | 22625
Cu (mg/L) | 0.61 – 1.46 | 1.1
𝐒𝐎𝟑 | 6.1 – 30.4 | 16
NH3–N (mg/L) | 7 – 21 | 13.75
COD (mg/L) | 800 – 1200 | 900
Total Solids (TS) (mg/L) | 2400 –3250 | 2825
Total Dissolved Solids (TDS) (mg/L) | 2270 – 2900 | 2580
Suspended Solids (TSS) (mg/L) | 120 – 400 | 260
Biochemical oxygen demand (BOD) | 115 – 235 | 175

## Slide 9: CONSTRAINTS AND COMPLEXITIES
Restrictions and the difficulty to test a sample from Al-jubail site.
Wastewater sample analysis
Temperature affects rate of reaction of most chemical and biological processes.
Climate constraints
Enough space for future expansion.
Close to dumping location.
Land constraints
Constraints

## Slide 10: CONSTRAINTS AND COMPLEXITIES
Soil conditions needs to be investigated to see if the soil is safe to build on it.
Suitability of soil condition
The resources that must be committed for a longer period of time.
Chemical requirements
Regular maintenance should be available in order to keep the tanks in a suitable condition.
Maintenance requirements
Constraints

## Slide 11: CONSTRAINTS AND COMPLEXITIES
Complexities
Data collection
Structural design process
Software modeling

## Slide 12: CODES AND SPECIFICATIONS
Ministry of Environment for Wastewater Management in K.S.A.
Royal Commission for Jubail and Yanbu.

## Slide 13: DESIGN METHODOLOGY
Plant Location
Design Period
Layout Plan

## Slide 14: PLANT LOCATION
Figure 4.1: The proposed location of the wastewater treatment plant in Al-Jubail (google maps)
N

## Slide 15: DESIGN PERIOD
The choice design period is based on:
Useful life based on wear and tear.
Expected industrial growth and developments.
Feasibility for addition or expansion.
Financial constraints and interest rate.
(Google Maps)

## Slide 16: LAYOUT PLAN
The basic rules used to develop wastewater treatment layout plan:
A site for wastewater treatment plant is proposed.
The preliminary layout of wastewater is made from the topographic map.
Considered that the trunk wastewater treatment should be located in a valley.
It is considered that the wastewater treatment plant should not be near water mains.

## Slide 17: ENVIRONMENTAL IMPACT ASSESSMENT
Different Environmental Parameters | Status | Comments
Land | OK | Enough space available for future expansion.
Location and Accessibility | OK | It's allowed to enter the site and no army and military sites around.
Soil Types or Condition | OK | Mostly sand.
Soil and Topography | OK | Shrubs will be cleared at the project location during the excavation work.
Table 5.1: The EIA Results and Status of the Proposed Site

## Slide 18: DESIGN CALCULATIONS
Yearly Population Growth Rate:
(worldometer, 2020)

## Slide 19: DESIGN CALCULATIONS
Flow Rate
Formula | Parameters | Description
𝒑 = 𝒑𝟎 × 𝟏 + 𝒊 𝒏 (Population) | 𝑝 = Future population 𝑝0 = Expected current population 𝑖 = Population growth rate 𝑛 = Time period | Estimation of flow rate
𝑸𝒐 = 𝒑 × 𝑸ሗ (Flow rate) | Qo: primary effluent flow rate (m3/day) 𝑝: Expected population. 𝑄ሗ : Average wastewater per capita | Estimation of flow rate
Flow Rate and Future Population (Formulas)

## Slide 20: DESIGN CALCULATIONS
Formula | Calculations
𝒑 = 𝒑𝟎 × 𝟏 + 𝒊 𝒏 (Future Population) | p = 60,000 × 1 + 0.0159 25 p = 89007 capita
𝑸𝒐 = 𝒑 × 𝑸ሗ (Flow Rate) | 𝑄 = 89007 × 240 𝑄 = 21361734 𝑙/𝑑𝑎𝑦 Maximum Flow Rate (𝑸𝑴𝒂𝒙): 21361734 𝑄𝑚𝑎𝑥 = = 21362 𝑚3/𝑑𝑎𝑦 1000
Flow Rate and Future Population (Calculations)

## Slide 21: DESIGN CALCULATIONS
Table 6.2: Main Parameters for Aeration Tank Design
Parameter | Annotation | Value | Unit | Ref
Primary effluent flow rate | Qo | 21362 | m3/day | (calculated)
Primary effluent biochemical oxygen demand | BOD | 175 | mg/L | (Table 6.1)
Concentration of dissolved pollutants such as BOD | So | 175 | mg/L | (Table 6.1)
Primary effluent suspended solids conc. | Xo | 260 | mg/L | (Table 6.1)
Aeration tank MLSS (suspended solids conc.) | X | 2000 | mg/L | (Harlan H.)
Volumetric loading | VL | 0.5 | kg BOD/day/m3 | (Harlan H.)
% volatile solids in the aeration tank mixed liquor suspended solid | %Vol. | 75 | % | (Harlan H.)

## Slide 22: DESIGN CALCULATIONS
Table 6.3: Aeration Tank Formulas
Equation | Parameters | Description
𝑸𝒐= 𝒑 × 𝑸ሗ | 𝑄𝑜: Primary effluent flow rate (m3/day) 𝑝: Expected population 𝑄ሗ : Average wastewater per capita | Estimation of flow rate
𝑽 = 𝑺𝒐 × 𝑸𝒐 𝑽𝑳 × 𝟏𝟎𝟎𝟎 | V: Aeration tank volume m3 So: Concentration of dissolved pollutants VL: Volumetric loading kg BOD/day/m3 | Estimation of aeration tank volume

## Slide 23: DESIGN CALCULATIONS
Table 6.3: Aeration Tank Formulas (continued)
Equation | Parameters | Description
𝑽 𝑯𝑹𝑻 = 𝟐𝟒 × 𝑸𝒐 | HRT: Hydraulic retention time hours V: Aeration tank volume m3 Qo: primary effluent flow rate (m3/day) | Estimation of hydraulic retention time
𝑭: 𝑴 = 𝑺𝒐 × 𝑸𝒐 % 𝑽𝑶𝑳 × 𝑿 × 𝑽 | F:M: Food to Microorganism ratio kg BOD/day/kg MLVSS % 𝑉𝑂𝐿: % volatile solids in the aeration tank mixed liquor suspended solid % So : Concentration of dissolved pollutants such as BOD mg/L Qo : primary effluent flow rate (m3/day) V : Aeration tank volume m3 X : aeration tank MLSS (suspended solids conc.) | Estimation of food to microorganis m ratio

## Slide 24: DESIGN CALCULATIONS
V =
So × Qo
=
VL × 1000 0.5 × 1000
175 × 21362
= 7476.7 m3
Using 3 aeration tanks (if we use less than 3 tanks the ratio between w/d and L will exceed the limits provided)
Volume for each aeration tank = 7476.7 / 3 = 2492.23 m3
Depth = 4 m (limit is from 3 to 5 m)
between w/d and L will exceed the limits provided:
Area for each Aeration tank = Volume / Depth = 2492.23/4 = 623 m2
Use a width / depth Ratio of 2 (W/D)= 2 Width = 2 * 4 = 8 m
Length of aeration tank = 623/8 = 77.88 m Use L = 80 m
Aeration Tank Design Calculations: Volume of the aeration tank required (Harlan H.):

## Slide 25: DESIGN CALCULATIONS
Aeration Tank Design Calculations (continued):
𝐻𝑅𝑇 = 24 ×
𝑉
𝑄𝑜
= 24 ×
7476.7
21362
= 8.4 ℎ𝑜𝑢𝑟𝑠
𝐹: 𝑀 =
𝑆𝑜 × 𝑄𝑜
% 𝑉𝑂𝐿 × 𝑋 × 𝑉
=
175 × 21362
0.75 × 2000 × 7476.7
= 0.333 kg BOD/day/kg MLVSS

## Slide 26: DESIGN CALCULATIONS Aeration Tank Summary
Parameters | Value
Length | 80 m
Width | 8 m
Depth | 4 m
Width/Depth Ratio | 2
Number of tanks | 3
Volume for each tank | 2560 m3
HRT | 8.4 h
F:M Ratio | 0.33 kg BOD/day/kg MLVSS

## Slide 27: DESIGN CALCULATIONS
Parameter | Range values (Al- Hammad) [4] | Selected/calculated values
Flow Rate (m3/day) | - | 21362
Detention time (𝒉) | 1.5-2.5 | 2
Length L (m) | 15-90 | 34.5
Width 𝐁 (𝒎) | 3-24 | 11.5
Depth 𝐃 (𝒎) | 3-5 | 4.5
Density of water 𝝆𝒘 (𝒌𝒈/𝒎𝟑) | - | 1000
Table 6.5: Sedimentation Tank Design Parameters

## Slide 28: DESIGN CALCULATIONS
Formula | Parameters | Description
𝑽 = 𝑸 × 𝑻 | V : Sedimentation tank volume m3 Q: Discharge “flow rate” m3/min. T : detention time (min) | Estimation tank volume
𝑨 = 𝑽 / 𝑫 | A : Area of the sedimentation tank V : Aeration tank volume m3 D : depth of the tank | Estimation of sedimentation tank area
𝝅 𝑨 = 𝑫𝟐 𝟒 | A : Area of the sedimentation tank D : diameter of the tank | Estimation of tank diameter
Formulas Used for Sedimentation Tank Design

## Slide 29: DESIGN CALCULATIONS
Formula | Parameters | Description
𝑔 × ( 𝜌𝑠 − 𝜌𝑤) 𝑉𝑠 = × 𝑑𝑠2 18 ʋ | Vs is the terminal settling velocity of the solid particle g is the gravitational acceleration ρs is the specific gravity of particles ρw is the specific gravity of water ds is the diameter of particle ʋ is the dynamic viscosity of water | Estimation of terminal settling velocity
8 𝛽 × 𝑔 × 𝑑𝑠 (𝜌𝑠 − 𝜌𝑤) 𝑉𝑐 = 𝑓 | Vc refers to the scouring velocity g is the acceleration due to gravity f is the Darcy Weisbach factor β is the constant d is the smallest particle | Estimation of scouring velocity
Formulas Used for Sedimentation Tank Design (continued)

## Slide 30: DESIGN CALCULATIONS
Diameter of the tank =
𝐴 =
𝜋
4
2
0.5 0.5
𝐷 → D = [(4*A) / 3.14] = [(4*98.8) / 3.14] = 11.2 m
𝑠
𝑉 =
𝑠 𝑤
𝑔 ×( 𝜌 −𝜌 )
18 ʋ
2
× 𝑑𝑠 =
9.81 ×( 2650−1000)
18 ×1.009 ×10−3
0.02
1000
2
× ( ) = 3.565 × 10
−4
𝑚/𝑠
𝑐
𝑉 =
8 𝛽 ×𝑔 ×𝑑𝑠 (𝜌𝑠−𝜌𝑤)
𝑓
=
8 ×0.05 ×9.81 ×0.02 (2650−1000)
0.03
= 65.7𝑚𝑚/𝑠 = 6.57 × 10−2 𝑚/𝑠
Sedimentation Tank Calculations:
Volume = discharge × time = 3.705 m3/min × 120 min = 444.6 m3 (volume of each tank)
Area = V / d = 444.6 m3 / 4.5 m = 98.8 m2

## Slide 31: DESIGN CALCULATIONS Table 6.6: Sedimentation Tank Design Parameters (Summary)
Parameters | Value
Diameter | 11.2 m
Depth | 4.5 m
Volume | 444.6 m3 each tank
Type | Circular
Number of tanks | 4

## Slide 32: DESIGN CALCULATIONS Formulas Used for Filtration Tank Design
Formula | Parameters | Description
𝑵 = 𝟏. 𝟐𝑸𝟎.𝟑 | N=Total Number of Filter Q=Maximum plant flow rate | Estimation number of filtration tanks required
𝑳/𝑩 | L: Length of the tank “m” B: Width of the tank “m” | Estimation of sedimentation tank dimension
𝜋 𝐴 = 𝐷2 4 | A: Total area of perforations D: Lateral diameter | Estimation of tank diameter
4 × A𝐡 𝑛 = 3.14 (𝑫𝒉)2 | n: Total no. of holes Ah: Area of the hole m2 Dh: Hole diameter m | Estimation of total no. of holes of laterals

## Slide 33: DESIGN CALCULATIONS Filtration Tank Design Summary
33
Parameters | Value
Length (L) | 8.5 m
Width (B) | 6.5 m
Type | Rectangular
Number of tanks | 2
Flow rate | 8 m/h
Area of each filter | 55.75 m2
Filter run time | 24 hours

## Slide 34: STRUCTURAL & HYDRAULIC DESIGN
Table 7.1: Summary of the Equation Used for Hydraulic Design of the Pipes
Equation | Parameters | Description
𝐐 = 𝐀 𝐕 | Q: flow rate (m3/s) A: area of the pipe (m2) V: velocity in the pipe (m/s) | Flow rate formula to find V
𝐀 = 𝛑/𝟒 × 𝐃^𝟐 | A: area of the pipe (m2) D: pipe diameter (m) | Area of pipe cross section
𝐩 = 𝛑 × 𝐃 | P = wetted perimeter (m) D= pipe diameter (m) | Wetted perimeter to find Rh
𝐀 𝐑𝐡 = 𝐩 | Rh = hydraulic radius (m) A = cross sectional area of flow (m2) P = wetted perimeter (m) | Hydraulic radius formula
34

## Slide 35: STRUCTURAL & HYDRAULIC DESIGN
Table 7.1: Summary of the Equation Used for Hydraulic Design of the Pipes
(continued)
𝑸 × 𝒏 𝟐 𝑺 = 𝑨 × 𝑲𝒏 × 𝑹𝟐/𝟑 | Q: flow rate (m3/s) V = cross-sectional mean velocity (m/s) kn = 1.0 for SI units n = Manning coefficient of roughness 𝑅ℎ= hydraulic radius (m) S = slope - or gradient of pipe (m/m) | Slope of the pipe required
35

## Slide 36: STRUCTURAL & HYDRAULIC DESIGN
Table 7.2: Summary of Hydraulic Design of the Pipe Connecting Aeration with Sedimentation Tank
Parameters | Value | Unit
Flow (Q) | 0.247 | m3/s
Diameter (D) | 1 | m
Area (A) | 0.5024 | m2
Velocity (V) | 0.314 | 𝑚/𝑠
Pipe slope | 0.00157 ~ 1:650 | m/m
Figure 7.1: Sketch of the pipe connecting aeration with sedimentation tank
V = 1 m
36
H = 650 m
D = 1 m

## Slide 37: STRUCTURAL & HYDRAULIC DESIGN
Parameters | Value
Length | 80 m
Width | 8 m
Depth | 4 m
4 m
3.5 m
Figure. 7.2: Pressure distribution and resultant force in an
open tank (Pieter Wesseling, 2001)
37
Structural Design of Aeration Tank
Aeration Tank Parameters

## Slide 38: STRUCTURAL & HYDRAULIC DESIGN
Structural Design of Aeration Tank
38
Parameters | Value
Pressure at the bottom of the wall ( P ) | 35 kN/m2
The force of this pressure ( F ) | 61.25 kN
Mmax | 71.5 kN.m
Steel area of aeration tank | 4#19 /m in each site

## Slide 39: STRUCTURAL & HYDRAULIC DESIGN
8 m
80 m
4 #19 / m
39
4 #19 / m
4 #19 / m
4 #19 / m
280 mm
280 mm
Structural Design of Aeration Tank
Table 7.4: Summary of structural design of aeration tank.
Figure 7.3: Steel reinforcement of aeration tank wall.
Parameters | Value
Area of the tank (A) | 640 m2
Wall thickness (d) | 280 mm
Area of steel used for walls (As) | 1136 mm2/m (4 # 19) / m
Total steel | 139.2906 ton
Total concrete | 591.36 m3

## Slide 40: STRUCTURAL & HYDRAULIC DESIGN
Parameters | Value
Water Height | 4.5 m
Diameter | 11.2 m
Soil Height | 3.0 m
40
Parameters | Value
𝛾𝑤𝑎𝑡𝑒𝑟 | 10 𝑘𝑁/𝑚3
𝛾𝑠𝑜𝑖𝑙 | 18 𝑘𝑁/𝑚3
𝛾𝑐𝑜𝑛𝑐𝑟𝑒𝑡𝑒 | 25 𝑘𝑁/𝑚3
Structural Design of Sedimentation Tank
Sedimentation Tank Parameters Design Parameters

## Slide 41: STRUCTURAL & HYDRAULIC DESIGN Case 1: Leakage Test
41
From table A-1, T=Coef*γ*H*R |  |  |  | 
From table A-2, M=Coef*γ*H3 |  |  |  | 
CASE 1: LEAKING TEST PRIOR TO BACKFILLING |  |  |  | 
Effect of Water Pressure |  |  |  | 
Point | T. Coef. | (T)(KN)*1.7*1.65 | M. Coef. | (M) (KN.m/m)*1.7*1.3
0H | 0.0035 | 2.427 | 0.0000 | 0.000
0.1H | 0.1115 | 77.317 | 0.0001 | 0.099
0.2H | 0.2260 | 156.715 | 0.0002 | 0.395
0.3H | 0.3395 | 235.419 | 0.0006 | 1.087
0.4H | 0.4420 | 306.496 | 0.0014 | 2.667
0.5H | 0.5190 | 359.890 | 0.0024 | 4.741
0.6H | 0.5445 | 377.572 | 0.0037 | 7.310
0.7H | 0.4885 | 338.740 | 0.0045 | 8.791
0.8H | 0.3410 | 236.460 | 0.0029 | 5.729
0.9H | 0.1315 | 91.186 | -0.0031 | -6.026
1.0H | 0.0000 | 0.000 | -0.0167 | -32.894

## Slide 42: STRUCTURAL & HYDRAULIC DESIGN Case 2: Soil Effect
42
From table A-1, T=Coef*γ*H*R*Ka |  |  |  | 
From table A-2, M=Coef*γ*H3*Ka |  |  |  | 
CASE 2: EMPTY TANK |  |  |  | 
Effect of soil pressure |  |  |  | 
Point | T. Coef. | (T)(KN)*1.7*1.3 | M. Coef. | (M) (KN.m/m)*1.7*1.3
0H | 0.0035 | -1.136 | 0.0000 | 0.000
0.1H | 0.1115 | -36.185 | 0.0001 | -0.059
0.2H | 0.2260 | -73.343 | 0.0002 | -0.235
0.3H | 0.3395 | -110.176 | 0.0006 | -0.645
0.4H | 0.4420 | -143.440 | 0.0014 | -1.584
0.5H | 0.5190 | -168.429 | 0.0024 | -2.816
0.6H | 0.5445 | -176.704 | 0.0037 | -4.342
0.7H | 0.4885 | -158.531 | 0.0045 | -5.222
0.8H | 0.3410 | -110.663 | 0.0029 | -3.403
0.9H | 0.1315 | -42.675 | -0.0031 | 3.579
1.0H | 0.0000 | 0.000 | -0.0167 | 19.539

## Slide 43: STRUCTURAL & HYDRAULIC DESIGN
Bars (Table B – 4) | As (mm2) | Min width used (Table B – 5) | Check | Selected As
8 # 10 | 568 | 341 < 1000 | OK | 
5 # 13 | 645 | 288 < 1000 | OK | Selected
3 # 16 | 597 | 219 < 1000 | OK | 
43
Design Reinforcement for Ring Tension
Tmax = 377 kN/m
The required reinforcement to resist this tensile force is:
𝐀𝐫𝐞𝐚 = 𝐓𝐦𝐚𝐱Τ( 𝟎. 𝟗 × 𝐅𝐲 )
= 377Τ( 0.9 × 420 ) = 998 mm2/m = 500 mm2/m /layer
Table 7.7: Selected steel area of ring tension in sedimentation tank

## Slide 44: STRUCTURAL & HYDRAULIC DESIGN
Design Reinforcement for Ring Tension
Design for Vertical Moment At the bottom wall:
Mu= 33 KN.m/m
From table A-5 in the appendix with fc’= 28 MPa and fy = 420 MPa Assume b = 250 mm
D = 250-50-6 = 194 mm
𝑀𝑢 33𝑥106
44
= 0.974
𝐾 = 𝛷 𝑏 × 𝑑2 = 0.9 × 1000 × 1942
Go to table B-9 (APPENDIX) to select the steel ratio:
ρ = 0.0024
Check max and min steel area, using Table B–7.
According to table B – 7, ρmin = 0.0033 > ρ → OK As = ρ x b x d = 0.0033 x 194 x 1000 = 640 mm2
Estimate No. of bars according to tables B – 4 and B – 5.

## Slide 45: STRUCTURAL & HYDRAULIC DESIGN
Bars (Table A – 4) | As (mm2) | Min width used (Table A – 5) | Check | Selected As
6 # 13 | 774 | 326 < 1000 | OK | Selected
4 # 16 | 796 | 260 < 1000 | OK | 
3 # 19 | 852 | 226 < 1000 | OK | 
45
Table 7.8: Selected steel area of vertical moment in sedimentation tank
Parameters | Value
Area of the tank | 𝜋𝑟2 = 98.4704 𝑚2
Steel area of ring tension in sedimentation tank | 5#13 /m
Steel area of vertical moment of sedimentation tank | 6#13/m
Total concrete | 78.24487 𝑚3
Total steel | 162.5606 ton
Summary of Sedimentation Tank Design:

## Slide 46: STRUCTURAL & HYDRAULIC DESIGN
Parameters | Value
Length (L) | 8.5 m
Width (B) | 6.5 m
Depth (D) | 3 m
Figure 7.10: Pressure distribution and resultant force in an open tank (Pieter Wesseling, 2001)
Structural Design of Filtration Tank
Filtration Tank Dimensions
3 m
2.5 m
46

## Slide 47: STRUCTURAL & HYDRAULIC DESIGN
Design Reinforcement of Filtration Tank
Figure 7.11: Steel reinforcement of filtration tank wall
4 #13 / m
47
4 #13 / m
4 #13 / m
4 #13 / m
200 mm
200 mm

## Slide 48: STRUCTURAL & HYDRAULIC DESIGN
Table 7.10: Summary of Structural Design of Filtration Tank.
48
Parameters | Value
Area of the tank (A) | 55.25 m2
Wall thickness (d) | 200 mm
Area of steel used for walls (As) | 516 mm2/m (4 # 16) / m
Total concrete | 36 m2
Total steel | 30.816 ton

## Slide 49: SOFTWARE MODEL
Figure 8.2: Aeration tank model on SAP2000
Aeration Tank Design SAP(2000)
Case 1: Leakage Test
Figure 8.4: Walls vertical moment from water effect
49

## Slide 50: SOFTWARE MODEL Sedimentation Tank Design (SAP 2000)
Figure 8.9: Vertical moment of sedimentation tank
68
98
84
70
56
42
28
14
0
-14
-28
-42
-56
-70
-84
50
Figure 8.12: Deflection of sedimentation tank (mm x10-6)

## Slide 51: SOFTWARE MODEL
Figure 8.13: Filtration tank model on SAP2000
Filtration Tank Design (SAP2000)
Figure 8.14: Walls vertical moment from water effect
51
26.4
24
21.6
19.2
16.8
14.4
12
9.6
7.2
4.8
2.4
0
-2.4
-4.8

## Slide 52: COST ESTIMATION OF WWTP
Summary of Cost Estimation of WWTP
The price of the cubic meter of concrete was taken from SAUDI READYMIX Company, and the steel price was taken from SABIC company as mentioned earlier.
Table 9.3: Summary of total cost of the tanks required for WWTP.
52
Element | Unit Price | Total amount calculated | Total price estimated
Concrete | 220 SAR per m3 | 705.605 m3 | 155233
Steel | 3105 SAR per ton | 332.67 ton | 1032940
Total (SAR) |  |  | 1,188,173 SAR

## Slide 53: SUMMARY AND CONCLUSION
WWTP
53
Aeration Tank
Sedimentation Tank
Filtration
Tank
The wastewater treatment plant consists of 3 main tanks. Which are aeration,
sedimentation and filtration tank.
The information we found allowed us to design WWTP that can help the industrial area and the surrounding factories
The structural design has been checked using SAP2000 program to perform the structural hand calculations, which gives almost the same values.

## Slide 54: REFERENCES
Moran, S. (2018). An Applied Guide to Water and Effluent Treatment Plant Design. Butterworth-Heinemann
Ilgi Karapinar Kapdan, Sabiha Alparslan, Application of anaerobic–aerobic sequential treatment system to real textile wastewater for color and COD removal, Enzyme and Microbial Technology, Volume 36, Issues 2–3, 2005,Pages 273-279,ISSN 0141-0229,https://doi.org/10.1016/j.enzmictec.2004.08.040.
Al-Hammad, Bushra & Abd El-Salam, Magda & Ibrahim, Sahar. (2014). Quality of wastewater reuse in agricultural irrigation and its impact on public health. Environmental monitoring and assessment. 186. 10.1007/s10661-014-3961-9.
Ouda, Omar. (2015). Treated wastewater use in Saudi Arabia: challenges and initiatives. International Journal of Water Resources Development. 32. 10.1080/07900627.2015.1116435.
Harlan H. Bengtson, PhD, P.E., Activated Sludge Calculations with Excel, Continuing Education and
Development, Inc. 9 Greyridge Farm Court.
“Wastewater formulas and conversion factors” published by Minnesota pollution control agency.
54

## Slide 55: REFERENCES
Davis, Mackenzie L. 2010. “Secondary Treatment By Suspended Growth Biological Processes, Chapter (McGraw- Hill Professional, 2010), Access Engineering.” Water and Wastewater Engineering: Design Principles and Practice.: 23-1- 23–115. http://bases.bireme.
Turki Bin Nasser Bin Abdulaziz. 2001. “Kingdom of Saudi Arabia Presidency of Meteorology and Environment-
‘General Environmental Regulations And Rules for Implementation.’” (October): 1–206.
The Wastewater Blog, “Food-to-Mass (F:M) Ratio”, December 2016. https://www.thewastewaterblog.com/single- post/2016/12/19/food-to-mass-ratio
Henze, M., van Loosdrecht, M. C. M., Ekama, G. A., & Brdjanovic, D. (2011). Biological Wastewater Treatment: Principles, Modelling and Design
Wastewater Filtration Design Considerations, PA Technology Transfer Seminar Publication, EPA-625/4-74-007a. ENVIRONMENTAL PROTECTION AGENCY Technology Transfer.
Al-Jasser, A. O. 2011. “Saudi Wastewater Reuse Standards for Agricultural Irrigation: Riyadh Treatment Plants Effluent Compliance.” Journal of King Saud University - Engineering Sciences 23(1): 1–8.
55

## Slide 56: REFERENCES
Pieter Wesseling. “Module1 : BASIC CONCEPTS AND PROPERTIES OF FLUIDS.” , 2001.
Design of Reinforced Concrete 10th Edition by Jack C. McCormac, Russell H. Brown, ACI Code Edition, 2018.
Portland Cement Association, PCA, Circular Concrete Tanks Without Prestressing, 2004.
Concerning Reality Nov, 21 , 2018. https://www.youtube.com/watch?v=0_ZcCqqpS2o&ab_channel=ConcerningReality
Collins Learning India, May 17, 2020. https://www.youtube.com/watch?v=s8IVjQg7yno&ab_channel=CollinsLearningIndia
56

## Slide 57
Department of Civil Engineering
57