## Slide 1: Design of Drinking Water Treatment Plant at New JUC Campus
Students Name & ID:
1-ABDULMOHSEN ALMOMEN
2-MOHAMMAD GHADER
3-HUSSAIN BUSALED
201400875
201503131
201502450
Advisor:
Dr. SAIDUR CHOWDHURY
Coordinator:
Dr. Andi Asiz

## Slide 2: 01. Introduction 02. Objective 03. Methodology 04. Environmental Design 05. Structural Design 06. References

## Slide 3: INTRODUCTION
What is water treatment?
Water treatment is any process that improves the quality of water to make it more acceptable for a specific end-use.
Treated Water follows the Drinking Water KSA Standard

## Slide 4: Water is a transparent liquid that is colorless, tasteless, and odorless Water is vital to humans and other living organisms Also, water is used for various purposes such as, agricultural. It is estimated that 70% of worldwide water is used for irrigation, with 15-35 % of irrigation withdrawals being unsustainable. It takes around 2,000 - 3,000 liters of water to produce enough food to satisfy one person's daily dietary need Water treatment is done in a series of stages. The conventional sequence goes from Filtration to Water Disinfection
Background

## Slide 5: Problem Statement
Water treatment plant is important as any other necessary facility to build in a population or a city. Every human being needs clean water in order to function normally.
A large area in the Jubail Industrial City at Al Firdous District is allocated to develop a new JUC campus. The new campus includes academic buildings (class rooms, laboratories, library and etc.) and residential area. The design population of the JUC new campus is 18,000.
A large number of dwellers living in this area require huge quantity of water for drinking as well as for other uses.

## Slide 6: Objectives
To select a suitable location for the proposed water treatment plant near the new JUC campus.
To decide about the source of water based on laboratory tests and literature review.
To determine the volume of underground water around the new JUC campus.
To estimate the amount of water during the design period of 20 to 25 years.
To design the water treatment units (-Coagulation-Flocculation-Sedimentation-Filtration and Disinfection) for the estimated water.

## Slide 7: METHODOLOGY Pre – Design Phase: Schematic Design Phase :
1-Population prediction
2-Decide the location of treatment plant.
3-The quality and availability of groundwater.
4-Decide about degree of Treatment.
1-Hydraulic Design
2-Environmental Treatment Process Design
3-Basic Structural Design.

## Slide 8: Typical characteristics for groundwater
Parameters | Groundwater characteristics | Treated water [10-11]
pH | 6.9 – 7.1 | 6.5-8.5
EC( da/m) | 0.92 – 0.98 | 0.15
TDS (mg/l) | 610 – 670 | 200
Total solids (mg/l) | 970 – 990 | 500
Ca (mg/l) | 15.4 – 18.7 | 10-12
Mg (mg/l) | 28.2 – 28.9 | 12-15
Na (mg/l) | 25.52 – 25.88 | 3-5
Cl (mg/l) | 48.71 – 49.2 | 43
K (mg/l) | 4.94 – 4.98 | 0.2-0.5
PO4 (mg/l) | 0.36 – 0.38 | 0.35-0.4
BOD (mg/l) | 2.0 - 2.2 | 0
COD (mg/l) | 2.8 - 3.0 | 0
Color (pt-co-units) | ND | 15
D.O (mg/l) | 5.9 - 6.1 | -
Coliform (MPN) | 5.8 – 12.5 | 3

## Slide 9: Water use for various purposes
WATER USE | VOLUME OF WATER
Avg. Water use in USA Bathing One shower Toilet Washing machines Kitchen sink Bathroom sink | 100 Gallon per day 30 – 40 Gallon 20 – 40 Gallon 5 Gallon per flush Avg. 25 Gallon per load 20 Gallon per day 15 Gallon per day

## Slide 10: Location
Al-Firdous District, Al Jubail
N

## Slide 11: Design Constraints and Operational Code
For any water treatment plant, major operational standards should be taken into account:
Performance Standards
Purpose and Scope
Water Source

## Slide 12: Environmental Design

## Slide 13: DESIGN METHODOLOGY
Expected population growth
Useful life based on wear and tear.
Feasibility for expansion.
Financial constraints and interest rate.

## Slide 14: Steps
Coagulation
Flocculation
Sedimentation
Filtration
Disinfection
Tank
Groundwater

## Slide 15: Estimation of Flow Rate

## Slide 16: Groundwater
75 ft
10-15 ft
Wells | Depth | Screen depth | Ground water level
1 | 75 ft | 15 ft | gravel
2 | 65 ft | 10 ft | sand
3 | 70 ft | 10 ft | clay
4 | 50 ft | 15ft | Silty clay

## Slide 17: Coagulation Tank

## Slide 18: Coagulation Tank

## Slide 19: Flocculation

## Slide 20: Flocculation Tank

## Slide 21: Coagulation and Flocculation
Parameters | Coagulation Tank | Flocculation Tank
Length | - | 4.6 m
Width/Diameter | 1.0 m | 1.53 m
Depth | 3 m | 4 m
Amount of Alum | 198725 kg/day | -
No. of Tanks | 2 | 6 tanks
Type | Circular | Square
Detention Time | 60 sec | 30 min
Flow | 0.25 m3/s | 0.25 m3/s
Table 1: Coagulation and Flocculation design parameters

## Slide 22: Sedimentation

## Slide 23: Design of Sedimentation Tank
Sedimentation, also known as settling or clarification is the process of removing solid particles by gravity. To design a clarification tank, we use the following:
Q = 0.25 m3/s
Using four sedimentation tanks.
Q per tank | Time | Volume | Depth | Area | Diameter | Settling velocity | Sourcing velocity
0.023m3/s | 2h | 165.6m3 | 4m | 41.4m2 | 7.26m | 3.59*104m/s | 64.7mm/s
Sedimentation design parameters

## Slide 24: Sedimentation
Parameters | Value
Diameter | 7.26 m
Depth | 4 m
Volume | 165.6 m3 each tank
Types | Circular
Number of tanks | 4
Slope of sludge zone | 1 : 6
Inlet zone | -
Outlet zone | 11
Table 2: Sedimentation tank design parameters

## Slide 25: Filtration

## Slide 26: Design of Filtration Tank

## Slide 27: Filtration
Table 3: filtration tank design parameters
Parameters | Value | Standard Ranges
length | 5.5 m | 4-8 m
Depth | 6 m | 
Width | 4.5 m | 
Type | rectangular | Rapid sand gravity filter
Number of tanks | 7 | -
Flow rate | 7 m/h | 7 – 20 m/h
No. of laterals | 37 per filter unit | -
Area of each filter | 25 m2 | 25 – 100 m2
Filter media | Sand and gravel | Sand and gravel
Effective size | 0.5 mm | 0.9 – 1.4 mm
Uniformly coefficient | 1.6 | 1.3 – 1.8
Filter media depth | 0.5 m | 0.3 – 0.75 m
Filter run time | 24 hours | -

## Slide 28: Disinfection
Volume = Q × time
Volume = 21600 m3/day × (1/24) × 0.5 h = 450 m3
Using effective depth of 4 m and length (L) = 2× width (W)
A = 450 m3/ 4 m = 112.5 m2
L × W = 112.5 m2
2 W × W = 112.5 m2
W^2 = 56.25 m2
W = 7.5 m and L = 2 × 7.5 = 15 m

## Slide 29: Disinfection
Table 4: disinfection tank design parameters
Parameters | Value
Width | 7.5m
Length | 15m
Depth | 4 m
Volume | 450 m3

## Slide 30
Hydraulic Design

## Slide 31: Hydraulic Design

## Slide 32: Hydraulic Design

## Slide 33
Structural Design

## Slide 34: STRUCTURAL ANALYSIS & DESIGN

## Slide 35: Storage Tank
Tank dimensions | Value in meter
Length | 60 ft = 18 m
Diameter | 60 ft = 18 m
Depths | 16 ft = 5 m
Table 5: Size of storage tank

## Slide 36: Storage Tank Stages

## Slide 37: Lower Well

## Slide 38: Lower Well

## Slide 39: Lower Well
 | Coefficient | 
top | 0.00 | 0.00
0.1H | 0.0002 | 118
0.2H | 0.0008 | 472
0.3H | 0.0016 | 944
0.4H | 0.0029 | 1711
0.5H | 0.0046 | 2714
0.6H | 0.0059 | 348
0.7H | 0.0059 | 348
0.8H | 0.0028 | 1655
0.9H | - 0.0058 | - 3421
bottom | - 0.0222 | - 13094
 | Coefficient | 
top | 0.00 | 0.00
0.1H | 0.0002 | 
0.2H | 0.0008 | 
0.3H | 0.0016 | 
0.4H | 0.0029 | 
0.5H | 0.0046 | 
0.6H | 0.0059 | 
0.7H | 0.0059 | 
0.8H | 0.0028 | 
0.9H | - 0.0058 | 
bottom | - 0.0222 | 

## Slide 40: Lower Well
Bars (Table A – 4) | As (in2) | Min width used (Table A – 5) | Check | Selected As
3 # 4 | 0.58 | 8.3 | OK | Selected
2 # 5 | 0.61 | 6.9 | OK | 
2 # 6 | 0.88 | 7 | OK | 

## Slide 41: Foundation/base slab

## Slide 42: Conclusion
The proposed water treatment plant will be helpful for actual design in future.
Quality of source water is suitable for use after treatment.
Filtration and disinfection with chlorine will provide required quality of water.
Hydraulic and structural design of water treatment plant was done.

## Slide 43: References
J. Fabregas, “Journal Pre-proof,” 2020.
J. Yang, S. Wang, Y. Li, Y. Zhang, and D. Xu, “Novel design concept for a commercial-scale plant for supercritical water oxidation of industrial and sewage sludge,” Journal of Environmental Management, vol. 233, no. October 2018, pp
https://www.livescience.com/47612-civil-engineering.html
https://www.emerald.com/insight/content/doi/10.1108/eb0489/full/html
S. Asian, “Design and Construction of Water-Treatment Plants on Novel Technology,” 2017.

## Slide 44: References
W. Is and T. Book, “Introduction: the nature of water and effluent treatment plant design,” pp. 1–12, 2018.
J. C. Lozier and J. W. Chapman, “Selection , design , and procurement of a demineralization system for a surface water treatment plant,” vol. 88, pp. 3–31, 1992.
Davis ML. Water and wastewater Engineering: Design principles and practice. 2011: McGraw-Hill Education, 2 Penn Plaza, New York, USA. ISBN 978-007-128924-5.

## Slide 45: THANK YOU